## OFS - As (All-in-one)
Work Instruction
Process Name: | GE Vernova Gas Power OFS Arsenic Contamination Standard Work Instruction. |  | Process owner: | Ross Conway
Task ID | Work Elements OFS-Determining Prescence of As | Who | Start Date | Due (*) Date | Key Points
1 | Determine fuel source for turbines associated with the Outage. | Service Manager | 3 months pre-outage | 1 months pre-outage | Any units combusting crude oil or Syngas will follow this standard work.
2 | Sample Parts | Site |  |  | If Arsenic contamaination is suspected
Task ID | Work Elements OFS-Contamination Zone | Who | Start Date | Due (*) Date | Key Points
ACTIVE 1 | Identify specific Active tasks where that can produce airborne Arsenic (i.e., any of the tasks below performed on surfaces of hot gas path components e.g., ) • Grinding • Sanding • Welding • Cutting • Blasting | Outage Manager | 3 months pre-outage | 1 months pre-outage | Conduct quantitative IH sampling to determine future controls. As instructed by GP Industrial Hygienst See Air Monitoring.
ACTIVE 2 | Establish contamination zone where active tasks are conducted. | Outage Manager | When active tasks are being performed |  | Arsenic contamination boundaries shall be established. These shall include: • Any area where there are Arsenic contaminated components. • Any area where contaminated tools are stored. • Any area where contaminated PPE is stored • Any area where there is exposed contaminated waste. • At a minimum, the contamination boundary must be 3m/10ft beyond the perimeter needed to perform the task.
ACTIVE 3 | Set-up restricted access to contamination boundaries. | Outage Manager | When active tasks are being performed |  | • Contamination zones should be barriered (access control) off and warning signs posted to restrict access to authorized personnel. • Barricade tape and tags should be supplied by Tooling Center. • RPE-required activities must cease whenever anyone enters this area without RPE.
ACTIVE 4 | Establish PPE requirements for entry into a contamination zone | Outage Manager/Site EHS | When active tasks are being performed |  | Active work at > 10% PEL: Personal Exposure action level would require RPE. • ACGIH: TLV-TWA 0.01 mg/m3 [10 ug/m3] • OSHA: 10 µg/m³ [5 µg/m³ Action Level] • OR Local/Regional/Country PEL/OEL IF More Stringent Reference PPE requirements section
ACTIVE 5 | Establish criteria for entry into contamination zone. | Outage Manager/Site EHS | When active tasks are being performed |  | Minimum training requirement for entry is completion of: • Arsenic Awareness (GE-EHS-119) • Respiratory Protection (GE-EHS-600)
ACTIVE 6 | Establish Air Monitoring in the contamination zone(s). | Outage Manager/Site EHS | When active tasks are being performed |  | Representative Industrial Hygiene Personal air monitoring should be performed. Under direction of Gas Power Industrial Hygienists
ACTIVE 7 | Declassifying contamination zones and removing access restrictions | Outage Manager/Site EHS | When active tasks are no longer being performed |  | Contamination zones can be declassified under the following conditions: When there is NO exposure to contaminated components or equipment.
PASSIVE 1 | Identify specific passive tasks that could produce ingestion or dermal exposure (i.e., any of the tasks below performed on surfaces of hot gas path components) • manual handling • storage • transportation • visual inspection | Outage Manager | 3 months pre-outage | 1 months pre-outage | Ensure PPE is approriate to work AND avoid direct contact with potential contamination expecially for any touch points
PASSIVE 2 | Establish contamination zone where active tasks are conducted. | Outage Manager | When passive tasks are being performed |  | Arsenic contamination boundaries shall be established. These shall include: Any area where hot gas path parts are handled or stored. At a minimum, the contamination boundary must be 3m/10ft beyond the perimeter needed to perform the task.
PASSIVE 3 | Set-up restricted access to contamination boundaries. | Outage Manager | When passive tasks are being performed |  | Contamination zones should be barriered (access control) off AND Warning signs posted to restrict access to authorized personnel. Barricade tape and tags should be supplied by Tooling Center.
PASSIVE 4 | Establish PPE requirements for entry into a contamination zone | Outage Manager/Site EHS | When passive tasks are being performed |  | Passive work does not require RPE to be worn. Reference PPE requirements
PASSIVE 5 | Establish criteria for entry into contamination zone. | Outage Manager/Site EHS | When passive tasks are being performed |  | Minimum requirement for entry is completion of: Arsenic Awareness course (GE-EHS-119)
PASSIVE 6 | Establish Air Monitoring in the contamination zone(s). | Outage Manager/Site EHS | When passive tasks are being performed |  | No air monitoring typically required in passive activity zones.
PASSIVE 7 | Declassifying contamination zones and removing access restrictions | Outage Manager/Site EHS | When passive tasks are no longer being performed |  | Contamination zones can be declassified under the following conditions: When there is no exposure to contaminated components or equipment.
Task ID | Work Elements OFS-Air Monitoring | Who | Start Date | Due (*) Date | Key Points
1 | If there is a potential for any active tasks to be performed, ensure respirator-certified personnel are available. | Service Manager | 3 months pre-outage | 1 months pre-outage | ADD THIS requirement to: • Outage Risk Profile (ORP) and • Outage Risk Review (ORR).
2 | Craft labor performing active task are subject to representative air monitoring. | Outage Manager / Business IH / Site EHS | When active tasks are being performed
3 | Send air samples to certified laboratory for analysis and Share results with GP Business IH. (ross.conway@gevernova.com) | Outage Manager/Site EHS | When active tasks are being performed |  | Business IH to evaluate data for further Gas Power sampling strategy
Task ID | Work Elements OFS - PPE Requirements | Who | Start Date | Due (*) Date | Key Points
1 PASSIVE: Activities | • To prevent skin exposure, additional PPE Required: • Disposable protective coveralls (e.g., Tyvek) • Disposable impermeable gloves (e.g., Nitrile, cut resistant) | Site EHS Representative | When passive tasks are being performed
2 ACTIVE: Activities | In addition to PASSIVE PPE requirement • RPE (masks) required for active tasks. | Site EHS Representative | When active tasks are being performed
3 | All disposable PPE (masks, gloves, coveralls) must be removed and disposed of in provided receptacle before leaving the contamination zone upon completion of task or work breaks. | Site EHS Representative | When/After tasks performed |  | See waste management
4 | Wash exposed body parts with soap and water immediately after PPE/RPE removal | Site EHS Representative | When tasks performed |  | Either close to work or enforced prior to entering eating areas
Task ID | Work Elements - OFS Decontamination | Who | Start Date | Due (*) Date | Key Points
1 | Use a damp cloth to clean the area of the part where active task work will be performed. | Craft Labour | Prior to active task being performed |  | Dispose of cloth in provided receptacle in the Contamination Zone.
Task ID | Work Elements OFS-Tool Management | Who | Start Date | Due (*) Date | Key Points
1 | Segregate tools used in contamination zones from clean tools. | Craft Labor | When work in the contamination zone is being performed.
2 | Tools used within contamination zones must be wiped with a damp cloth prior to leaving the contamination zone and upon declassifying of the contamination zone. | Craft Labor | When work in the contamination zone is being performed. |  | Dispose of cloth in provided receptacle in the Contamination Zone.
Task ID | Work Elements OFS-Waste Management | Who | Start Date | Due (*) Date | Key Points
1 | Communicate potential arsenic contamination to Customer. | Service Manager | 3 months pre-outage | 1 months pre-outage | Explain to Customer that, based on fuel type, the site will generate waste containers with PPE and wipes used that may be contaminated with arsenic.
2 | Coordinate disposal of Contamination Zone receptacles with Customer | Site EHS Representative | When contamination zones are declassified |  | Explain to Customer that waste containers may have arsenic contamination.
Task ID | Work Elements OFS-Training | Who | Start Date | Due (*) Date | Key Points
1 | Provide GE Vernova Arsenic Awareness training to all workers affected by this standard work. | Craft Labor / Site EHS | Prior to any Active or Passive tasks |  | Minimum training requirement for entry is completion of: • Arsenic Awareness (GE-EHS-119) • Respiratory Protection (GE-EHS-600) AND Site Specific Training to comply with the requirement of this standard Work
2 | Provide any site specific training | Sie EHS | Prior to any Active or Passive tasks |  | • Train workers on establishing a Contamination Zone. • Train workers in correct donning and doffing of additional PPE. • Train workers on correct disposal of spent PPE.
Task ID | Work Elements OFS-Shipping parts | Who | Start Date | Due (*) Date | Key Points
1 | Ensure fuel type is selected in RDM. Demand Placement tab > Installed Base Information. | CPM | 1 Year pre-outage |  | RDM will flag the job based on the fuel type.
2 | Use GE Vernova generated label and ensure proper coding is in place to indicate potential arsenic contamination. | CPM | When shipping parts. |  | • Consult with business logistics to confirm regulations for transportation. •Consider movement across jurisdictional boundaries. (State AND/OR Country)
Task ID | Work Elements OFS-Communications | Who | Start Date | Due (*) Date | Key Points
1 | Communicate arsenic precautions to Customer. | Service Manager | 3 months pre-outage | 1 months pre-outage | Inform the customer that additional waste stream will be generated that may contain arsenic.
2 | Communicate to Service Centers that potential arsenic contaminated parts are being shipped for repairs. | CPM | 1 Year pre-outage |  | Verify RDM fuel selection reflects Syngas or crude oil to accurately trigger arsenic notification functionality.
3 | Communicate arsenic precautions to Craft Labor. | Site EHS | Prior to any Active or Passive tasks |  | See Training section
Task ID | Work Elements OFS-Contract EHS T&C | Who | Start Date | Due (*) Date | Key Points
1 | Add condition to contract that HGP parts from crude or syngas service would be handled as arsenic-contaminated. | CPM | 1 Year pre-outage |  | Craft labour will have training and PPE for HGP work. Potential arsenic-contaminated material (e.g., PPE, cleaning wipes) will be collected for Customer to manage as waste. Communicate this to the Outage Risk Profile (ORP) and Outage Risk Review (ORR).