## OFS - As (All-in-one)
Work Instruction
Process Name: | GE Vernova Gas Power OFS Arsenic Contamination Standard Work Instruction. |  | Process owner: | Ross Conway
Task ID | Work Elements OFS-Determining Prescence of Pb | Who | Start Date | Due (*) Date | Key Points
1 | DETERMINE if there is a potential for Lead Contamination on generator. | Service Manager | 3 months pre-outage | 1 months pre-outage | • IF the generator falls within the scope of TIL1163-2 • THEN Lead sampling and management protocols need to be prepared. • No previous sampling or customer awareness shall be a decision point.
2 | Take initial wipe sample and send it to lab once the man cover is off. | Lead TFA | After LOTO applied | Before endshield is removed | • No internal work on generator or any entry in the area is allowed until the results are returned from lab.
3 | INTERPRETING LAB RESULTS On receipt of laboratory results determine if Lead contamination standard work instruction needs to be fully implemented. A confirmation of Lead surface contamination would require this standard work instruction to be followed. | GEV Qualified Industrial Hygenist (or EHS upon QIH approval) | On receipt of analysis results |  | • IF results confirm Lead contamination is above 200ug/ft2 then field team involved into the dissassembly have to follow standard work instruction and set up contamination zone. * No active work is allowed.
4 | 2nd Phase of SAMPLING of potentially contaminated units Wipe samples shall be taken from the areas identified in Diagram 1 (Stator) and Diagram 2 (Rotor) in accordance with instructions issued by the GEV Certified Industrial Hygienist. | Lead TFA | Once the field is out |  | o The standard sampling strategy for IH consultants OR Customers on site to follow OR methodology for obtaining samples by outage team: Insert here GE Vernova Gas Power sampling strategy
5 | SEND the wipe samples to a certified laboratory for analysis. | GEV Qualified Industrial Hygenist (or EHS upon QIH approval) | Outage day 1 |  | Potentially Lead contaminated parts must be treated as Lead contaminated until laboratory results confirm otherwise. Further sections of this Standard Work Instruction should be followed until result confirm not contaminated
6 | INTERPRETING LAB RESULTS On receipt of laboratory results determine if Lead contamination standard work instruction needs to be fully implemented. A confirmation of Lead surface contamination would require this standard work instruction to be followed. | GEV Qualified Industrial Hygenist (or EHS upon QIH approval) | On receipt of analysis results |  | If results confirm Lead contamination is above 200ug/ft2 then components being shipped off site shall be decontaminated as per this work instruction and resampled to confirm levels below 200ug/ft2. If results confirm Lead contamination at any level then this Standard Work Instruction should be followed.
7 | IF the results indicate >200ug/ft2 Lead Set up (de)contamination zone | Lead TFA/Regional Manager | On receipt of analysis results |  | Link to Contamination Zone
Task ID | Work Elements OFS-Contamination Zone | Who | Start Date | Due (*) Date | Key Points
1 | Determine Lead contamination zone boundaries. | TFA | After interpretation of lead results | Within a shift | Lead contamination boundaries shall be established in all areas where there is the potential for lead exposure. These shall include: • Any area where there are lead contaminated components. • Any area where contaminated tools are stored. • Any area where contaminated PPE is stored. • Any area where there is exposed contaminated waste.
2 | Set-up restricted access to contamination boundaries. | TFA | After interpretation of lead results | Within a shift | *Contamination zones should be barriered off and warning signs posted to restrict access to authorised personnel. *Authorized personnel shall have respirator medical clearance (if required by local regulation), fit test and any additional regulatory requirements).
3 | Establish PPE requirements for entry into a contamination zone. | TFA/EHS | After interpretation of lead results | Within a shift | Active work at any contamination level would require RPE Passive work does not require RPE Both Passive and Active work at any level would require all other PPE measures. Reference PPE requirements section of standard work.
4 | Establish whether Air Monitoring is required in the contamination zone(s). | Regional EHS | After interpretation of lead results | Within a shift | * Determine the need for air monitoring. * Consult GEV QIH for practices.
5 | Declassify contamination zones and remove access restrictions | Regional EHS | ASAP after IH results. |  | *Consult GEV QIH for practices. Contamination zones can be declassified under the following conditions: • Wipe Analysis results confirm no contamination. • When there is no exposure to contaminated components or equipment • (outage complete)
Task ID | Work Elements OFS-Air Monitoring | Who | Start Date | Due (*) Date | Key Points
1 | Determine which workers are “affected” and require personal air monitoring. | Regional EHS | Before specific active/aggressive work tasks that can produce airborne lead (e.g., abrasive grinding, sanding, welding, dry sweeping, compressed air use) |  | • In consultation with the GEV QIH.
2 | Fit and deploy personal air monitors for selected workers. | IH Consultant | Before specific active/aggressive work tasks that can produce airborne lead (e.g., abrasive grinding, sanding, welding, dry sweeping, compressed air use)
3 | Send air samples to certified laboratory for analysis | IH Consultant | After specific active/aggressive work tasks that can produce airborne lead (e.g., abrasive grinding, sanding, welding, dry sweeping, compressed air use) has been performed |  | • Request fast turn around time from laboratory.
4 | Use air monitoring results to classify/declassify or reduce contaminated zones | Regional EHS | Upon receiving the lab results |  | • Refer to GP IH Air Monitoring Plan. • Consult GEV QIH for practices.
Task ID | Work Elements OFS-PPE Requirements | Who | Start Date | Due (*) Date | Key Points
1 | Identify specific active/aggressive work tasks that can produce airborne lead (e.g., abrasive grinding, sanding, welding, dry sweeping, compressed air use) | TFA/Supervisor | Before work task implementation. |  | • Where active/aggressive tasks are carried RPE is required
2 | Issue Respirator Protective Equipment (RPE), if required, to personnel who have had face‑fit testing (clean shaven) before issuing respirators, unless they are issued with PAPR (Powered Air Purifying Respitators) | Site EHS/Supervisor | Before work task implementation. |  | • Medical Clearance should be done before Fit test if required by local regulation. • Face fit testing can only be carried out by trained personnel. •PAPR doesn't require fit test.
3 | Supply clean Type 5/6 disposable coveralls to all personnel entering into a contamination zones. | Site EHS/Supervisor | Before work task implementation. |  | • Shall be removed and disposed of as contaminated waste before leaving the contamination zone in communication with Customer. No reuse.
4 | Supply single use nitrile gloves to be worn under hand protection defined by task risk assessment. | Site EHS/Supervisor | Before work task implementation. |  | Nitrile gloves shall be: • Replaced immediately if torn. • Replaced every four hours at a minimum. • Removed and disposed of as contaminated waste before leaving the contamination zone.
5 | Overshoes (if not the part of the disposable coverall) | Site EHS/Supervisor | Before work task implementation.
6 | All disposable PPE (masks, gloves, coveralls and overshoes) must be removed and disposed of as contaminated waste before leaving the contamination zone. | Site EHS/Supervisor | After completion of the task. |  | • Consult customer. Refer to Waste section of Standard work.
7 | Wash exposed body parts with soap and water immediately after PPE removal | All Personnel | After completion of the task.
Task ID | Work Elements OFS-PPE Decontamination | Who | Start Date | Due (*) Date | Key Points
1 | For parts leaving the site refer to Shipping parts section of standard work for timeline. | TFA | As needed |  | • Decontamination of shipping parts is the responsibility of the Customer. • EXCEPTION: In some cases Customer can ask GEV team to assist with decontamination. Refer to GEV GP Decontamination Method for information.
2 | Customer shall identify the decontamination area. | TFA | Once the contamination zone is established |  | • The decontamination of any parts is the responsibility of the Customer. • Ensure the decontamination activities do not impact ajacent operations. • EXCEPTION: In some cases Customer can ask GEV team to assist with decontamination. • Refer to GEV GP Decontamination Method for information.
3 | Proceed with decontamination once all the control measures are in place under the supervision of GEV TFA. | TFA | Once the contamination zone is established |  | • Use GEV GP Decontamination Method. • Simple Green or equivalent detergent shall be used.
Task ID | Work Elements OFS-PPE Tool Management | Who | Start Date | Due (*) Date | Key Points
1 | Segregate tools used in contamination zones from clean tools. | Craft Supervisor | Before decontamination activities. | End of decontamination activities. | • Tools shall remain in contamination zone until Step 2 is followed.
2 | Tools can be declassified as contaminated if washed down with cleaning agent. | Craft Supervisor | End of decontamination activities. |  | • Cleaning agent - wipes, soap, detergent.
3 | Decontaminated Tools should be returned to the main tool storage. | Craft Supervisor | End of decontamination activities.
Task ID | Work Elements OFS-Waste Management | Who | Start Date | Due (*) Date | Key Points
1 | Identify all contaminated or potentially contaminated disposable products (PPE, wipes, etc.). | Craft Supervisor/TFA | End of decontamination activities. |  | • All activities must be coordinated with Customer. • Ensure they are stored in locally available labelled waste containers.
2 | Collect and containerize all potentially contaminated cleaning material. Immediately transfer all used cleaning materials and PPE to an appropriate, compatible, closed container designated for this waste stream. | Craft Supervisor/TFA | End of decontamination activities. |  | • Do not add any materials to this container that are not related to this task. • If there is a significant amount of liquid solution generated, keep it in a separate closed head drum. Follow instructions provided by Customer.
3 | Label containers in accordance with customer requirements unless customer is responsible for labeling. | Craft Supervisor | End of decontamination activities. |  | • All activities must be coordinated with Customer. • Containers should be labeled immediately.
4 | Store container(s) in areas designated by customer unless customer is responsible for moving the waste. | Craft Supervisor | End of decontamination activities. |  | • Customer is responsible for complying with storage regulations.
Task ID | Work Elements OFS-Training | Who | Start Date | Due (*) Date | Key Points
1 | Provide GE Vernova Lead Awareness training to all supervised workers working with or around contaminated parts. | Site EHS | Prior to work. |  | • Consider refresher training. • EHS is responsible to identify and assign proper category in GEV Learning.
2 | Provide any local specific training requirements. Follow local regulation if additional Lead certification is needed. | Site EHS | Prior to work.
3 | Train workers in correct donning and doffing of additional PPE. | Site EHS | Prior to work.
4 | Where PAPR is used then wearers should be trained and for RPE face fit testing must be complete. | Site EHS | Prior to work.
5 | Train workers on correct disposal of used PPE. | Site EHS | Prior to work.
Task ID | Work Elements OFS-Shipping parts | Who | Start Date | Due (*) Date | Key Points
1 | Confirm that Lead contamination is below 200ug/ft2 on the part. | TFA | Timeline agreed with the shop. |  | Post/after decontamination and sampling/analysis shall be required if initial results are above 200ug/ft2.
2 | Notify receiving GE Vernova Repair facility of analysis results | TFA | Timeline agreed with the shop. |  | Results should be sent to the receiving facility EHS, and Business IH and confirmation should be sent back to OFS Outage Manager that the repair facility is willing and prepared to accept the components.
3 | Package/wrap parts to prevent cross contamination | TFA/Supervisor | Before shipment |  | Parts should be packaged and/or wrapped to prevent cross contamination of people and environment (rain etc..) during shipping.
4 | Label parts and confirm transportation is managed within regulatory requirements | TFA | Before shipment |  | Consult with business logistics to confirm regulations for transportation. Consider movement across jurisdictional boundaries.
6 | Ship components | TFA | NA |  | Liaise with receiving repair centre as per standard procedures.
Task ID | Work Elements OFS-Communication | Who | Start Date | Due (*) Date | Key Points
1 | Communicate the lead potential presence and sampling need once identified during planning outage phase. | CSM | 3 months pre-outage | 1 months pre-outage | • Communication goes to outage TFA or customer (if forced shutdown)
2 | Post lab results close to work area and communicate results to employees. | TFA | After interpretation of lead results
Task ID | Work Elements OFS-Contract EHS Ts&Cs | Who | Start Date | Due (*) Date | Key Points
1 | The lead contamintion of the part being shipped to the shop for repairs shall be with lead contamination level below 200 ug/ft2. | Commercial | NA
2 | Include decontamination cost into job cost estimate (JCE). | Commercial | NA
3 | Include decontamination responsibilities into service agreement distribution of responsibilities | Commercial | NA
1 | If there is a potential for any active tasks to be performed, ensure respirator-certified personnel are available. | Service Manager | 3 months pre-outage | 1 months pre-outage | ADD THIS requirement to: • Outage Risk Profile (ORP) and • Outage Risk Review (ORR).
2 | Craft labor performing active task are subject to representative air monitoring. | Outage Manager / Business IH / Site EHS | When active tasks are being performed
3 | Send air samples to certified laboratory for analysis and Share results with GP Business IH. (ross.conway@gevernova.com) | Outage Manager/Site EHS | When active tasks are being performed |  | Business IH to evaluate data for further Gas Power sampling strategy
Task ID | Work Elements OFS - PPE Requirements | Who | Start Date | Due (*) Date | Key Points
1 PASSIVE: Activities | • To prevent skin exposure, additional PPE Required: • Disposable protective coveralls (e.g., Tyvek) • Disposable impermeable gloves (e.g., Nitrile, cut resistant) | Site EHS Representative | When passive tasks are being performed
2 ACTIVE: Activities | In addition to PASSIVE PPE requirement • RPE (masks) required for active tasks. | Site EHS Representative | When active tasks are being performed
3 | All disposable PPE (masks, gloves, coveralls) must be removed and disposed of in provided receptacle before leaving the contamination zone upon completion of task or work breaks. | Site EHS Representative | When/After tasks performed |  | See waste management
4 | Wash exposed body parts with soap and water immediately after PPE/RPE removal | Site EHS Representative | When tasks performed |  | Either close to work or enforced prior to entering eating areas
Task ID | Work Elements - OFS Decontamination | Who | Start Date | Due (*) Date | Key Points
1 | Use a damp cloth to clean the area of the part where active task work will be performed. | Craft Labour | Prior to active task being performed |  | Dispose of cloth in provided receptacle in the Contamination Zone.
Task ID | Work Elements OFS-Tool Management | Who | Start Date | Due (*) Date | Key Points
1 | Segregate tools used in contamination zones from clean tools. | Craft Labor | When work in the contamination zone is being performed.
2 | Tools used within contamination zones must be wiped with a damp cloth prior to leaving the contamination zone and upon declassifying of the contamination zone. | Craft Labor | When work in the contamination zone is being performed. |  | Dispose of cloth in provided receptacle in the Contamination Zone.
Task ID | Work Elements OFS-Waste Management | Who | Start Date | Due (*) Date | Key Points
1 | Communicate potential arsenic contamination to Customer. | Service Manager | 3 months pre-outage | 1 months pre-outage | Explain to Customer that, based on fuel type, the site will generate waste containers with PPE and wipes used that may be contaminated with arsenic.
2 | Coordinate disposal of Contamination Zone receptacles with Customer | Site EHS Representative | When contamination zones are declassified |  | Explain to Customer that waste containers may have arsenic contamination.
Task ID | Work Elements OFS-Training | Who | Start Date | Due (*) Date | Key Points
1 | Provide GE Vernova Arsenic Awareness training to all workers affected by this standard work. | Craft Labor / Site EHS | Prior to any Active or Passive tasks |  | Minimum training requirement for entry is completion of: • Arsenic Awareness (GE-EHS-119) • Respiratory Protection (GE-EHS-600) AND Site Specific Training to comply with the requirement of this standard Work
2 | Provide any site specific training | Sie EHS | Prior to any Active or Passive tasks |  | • Train workers on establishing a Contamination Zone. • Train workers in correct donning and doffing of additional PPE. • Train workers on correct disposal of spent PPE.
Task ID | Work Elements OFS-Shipping parts | Who | Start Date | Due (*) Date | Key Points
1 | Ensure fuel type is selected in RDM. Demand Placement tab > Installed Base Information. | CPM | 1 Year pre-outage |  | RDM will flag the job based on the fuel type.
2 | Use GE Vernova generated label and ensure proper coding is in place to indicate potential arsenic contamination. | CPM | When shipping parts. |  | • Consult with business logistics to confirm regulations for transportation. •Consider movement across jurisdictional boundaries. (State AND/OR Country)
Task ID | Work Elements OFS-Communications | Who | Start Date | Due (*) Date | Key Points
1 | Communicate arsenic precautions to Customer. | Service Manager | 3 months pre-outage | 1 months pre-outage | Inform the customer that additional waste stream will be generated that may contain arsenic.
2 | Communicate to Service Centers that potential arsenic contaminated parts are being shipped for repairs. | CPM | 1 Year pre-outage |  | Verify RDM fuel selection reflects Syngas or crude oil to accurately trigger arsenic notification functionality.
3 | Communicate arsenic precautions to Craft Labor. | Site EHS | Prior to any Active or Passive tasks |  | See Training section
Task ID | Work Elements OFS-Contract EHS T&C | Who | Start Date | Due (*) Date | Key Points
1 | Add condition to contract that HGP parts from crude or syngas service would be handled as arsenic-contaminated. | CPM | 1 Year pre-outage |  | Craft labour will have training and PPE for HGP work. Potential arsenic-contaminated material (e.g., PPE, cleaning wipes) will be collected for Customer to manage as waste. Communicate this to the Outage Risk Profile (ORP) and Outage Risk Review (ORR).